## README
PowerForge Phase 5 — Canonical Equipment Attribute Registry (registry-v1 candidate)
Purpose | Editable first-pass registry for the Phase 5 canonical engineering model.
Scope | 20 canonical equipment types. Each equipment type has its own worksheet.
Required? | Yes means unconditionally required for a minimally useful canonical model. Conditionally required attributes remain No here and are governed by Requirement Group / Requirement Condition and the Requirement Rules sheet.
Critical? | Missing data may materially limit or affect one or more engineering studies.
Conditional Requirements | Requirement Rules contains machine-readable ANY_OF, ALL_OF, REQUIRED_IF, and ALL_OR_NONE rules. Conditional fields are not individually marked Required=Yes.
Canonical Unit | Each attribute definition owns its canonical storage unit. Unit Families defines compatible dimensions/conversions and a default unit only; it does not override the attribute-level canonical unit.
Allowed / Enum Values | Semicolon-separated proposed enum values. Edit freely.
Not included | Calculated study outputs such as fault duty, incident energy, load-flow current, voltage drop, coordination margin, etc.
Taxonomy note | Registry contains 20 canonical equipment types. Disconnects are represented by SINGLE_THROW_SWITCH plus FUSE where applicable; bus assemblies are represented by BUS with bus_type.
Phase 5 architecture note | Equipment containment (e.g., breaker belongs to switchgear) may warrant parent_equipment_id; this is separate from electrical topology.
Protection settings note | Flat breaker/relay attributes cover the common first-pass case. Advanced multi-stage protection functions should eventually get a dedicated structured model rather than phase_oc_pickup_2, etc.
Registry policy | Canonical equipment/attribute keys are registry-controlled. AI extraction should not invent arbitrary canonical keys.
Version | registry-v1 candidate — conditional requirements, power-quantity naming, load representations, and unit semantics reconciled.

## Unit Families
Family | Default Unit | Supported Input Units | Notes
Voltage | kV | V; kV; MV | Attribute definition owns the canonical storage unit; this is only the family default.
Current | A | A; kA | Attribute definition owns the canonical storage unit; this is only the family default.
Fault current | kA | A; kA | Attribute definition owns the canonical storage unit; this is only the family default.
Apparent power | kVA | VA; kVA; MVA | VA is valid as an attribute canonical unit (e.g. CT/relay burden).
Active power | kW | W; kW; MW; hp | hp conversion is allowed only where semantically appropriate.
Reactive power | kvar | var; kvar; Mvar
Resistance / Reactance / Impedance | Ω | mΩ; Ω; kΩ
Impedance per length | Ω/km | Ω/m; Ω/km; Ω/1000 ft
Length | m | mm; cm; m; km; in; ft | An attribute may canonically store mm (e.g. electrode gap/enclosure dimensions).
Time | s | ms; s | An attribute may canonically store ms (e.g. trip/output operating time).
Frequency | Hz | Hz
Speed | rpm | rpm
Capacitance | µF | nF; µF; mF
Inductance | mH | µH; mH; H
Percentage | % | %
Temperature | °C | °C; °F
Per unit | p.u. | p.u. | Dimensionless per-unit quantity; base quantities are carried separately when needed.

## Utility Source
UTILITY SOURCE
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
nominal_voltage | Nominal Voltage (kV) | NUMBER | kV | Yes | Yes |  | Usually 24.94kV or 12.47kV
phase_count | Phase Count | INTEGER |  | Yes | Yes |  | Usually 3
fault_data_basis | Source Data Basis | ENUM |  | No | No | FAULT_CURRENT; SEQUENCE_IMPEDANCE; BOTH;
three_phase_fault_current | 3-Phase Fault Current (kA) | NUMBER | kA | No | Yes |  |  |  | UTILITY_FAULT_DATA:A | Always for a study-ready utility short-circuit source.
slg_fault_current | Line-to-Ground Fault Current (kA) | NUMBER | kA | No | Yes |  |  |  | UTILITY_FAULT_DATA:A | Always for a study-ready utility short-circuit source.
three_phase_x_r | 3-Phase X/R Ratio | NUMBER |  | No | Yes |  |  |  | UTILITY_FAULT_DATA:A | Always for a study-ready utility short-circuit source.
slg_x_r | Single Line-to-Ground X/R Ratio | NUMBER |  | No | Yes |  |  |  | UTILITY_FAULT_DATA:A | Always for a study-ready utility short-circuit source.
positive_sequence_resistance | Positive Sequence Resistance (Ω) | NUMBER | Ω | No | Yes |  |  |  | UTILITY_FAULT_DATA:B | Always for a study-ready utility short-circuit source.
positive_sequence_reactance | Positive Sequence Reactance (Ω) | NUMBER | Ω | No | Yes |  |  |  | UTILITY_FAULT_DATA:B | Always for a study-ready utility short-circuit source.
zero_sequence_resistance | Zero Sequence Resistance (Ω) | NUMBER | Ω | No | Yes |  |  |  | UTILITY_FAULT_DATA:B | Always for a study-ready utility short-circuit source.
zero_sequence_reactance | Zero Sequence Reactance (Ω) | NUMBER | Ω | No | Yes |  |  |  | UTILITY_FAULT_DATA:B | Always for a study-ready utility short-circuit source.

## Synchronous Generator
SYNCHRONOUS GENERATOR
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
phase_count | Phase Count | INTEGER |  | No | Yes |  |  | Typically 3
rated_apparent_power | Rated Apparent Power (kVA) | NUMBER | kVA | Yes | Yes
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
rated_power_factor | Rated Power Factor | NUMBER |  | Yes | Yes |  | pf | Ranges from 0-1
rated_speed | Rated Speed (rpm) | NUMBER | rpm | No | No
pole_count | Pole Count | INTEGER |  | No | No
reactance_base_power | Alternator Base Power (kVA) | NUMBER | kVA | No | Yes |  |  | Required if reactance values are based on it and it's different than rated value | GEN_REACTANCE_BASE_POWER | Per-unit reactances are stated on a base power different from rated_apparent_power.
reactance_base_voltage | Alternator Base Voltage (kV) | NUMBER | kV | No | Yes |  |  | Required if reactance values are based on it and it's different than rated value | GEN_REACTANCE_BASE_VOLTAGE | Per-unit reactances are stated on a base voltage different from rated_voltage.
xd | Direct-axis Synchronous Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | Xd | Machine base value
xq | Quadrature-axis Synchronous Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | Xq | Machine base value
xd_transient | Direct-axis Transient Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | X'd | Machine base value
xq_transient | Quadrature-axis Transient Reactance (p.u.) | NUMBER | p.u. | No | No |  | X'q | Machine base value
xd_subtransient | Direct-axis Subtransient Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | X''d | Machine base value
xq_subtransient | Quadrature-axis Subtransient Reactance (p.u.) | NUMBER | p.u. | No | No |  | X''q | Machine base value
negative_sequence_reactance | Negative Sequence Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | X2 | Machine base value
zero_sequence_reactance | Zero Sequence Reactance (p.u.) | NUMBER | p.u. | Yes | Yes |  | X0 | Machine base value
tdo_transient | Direct-axis Transient Open-circuit Time Constant (s) | NUMBER | s | No | No |  | T'do
tdo_subtransient | Direct-axis Subtransient Open-circuit Time Constant (s) | NUMBER | s | No | No |  | T''do
tqo_transient | Quadrature-axis Transient Open-circuit Time Constant (s) | NUMBER | s | No | No |  | T'qo
tqo_subtransient | Quadrature-axis Subtransient Open-circuit Time Constant (s) | NUMBER | s | No | No |  | T''qo
armature_time_constant | Armature Time Constant (s) | NUMBER | s | No | No |  | Ta | Armature/stator DC time constant
armature_resistance | Armature Resistance (Ω) | NUMBER | Ω | Yes | Yes |  | Ra | Also known as stator winding resistance
negative_sequence_resistance | Negative-sequence Resistance (Ω) | NUMBER | Ω | No | Yes |  | R2
zero_sequence_resistance | Zero-sequence Resistance (Ω) | NUMBER | Ω | No | Yes |  | R0
grounding_configuration | Grounding Configuration | ENUM |  | No | Yes | SOLID; RESISTANCE; REACTANCE; UNGROUNDED; UNKNOWN
grounding_resistance | Grounding Resistance (Ω) | NUMBER | Ω | No | Yes |  | Rn | Value depends on grounding configuration | GEN_GROUNDING_RESISTANCE | grounding_configuration = RESISTANCE
grounding_reactance | Grounding Reactance (Ω) | NUMBER | Ω | No | Yes |  | Xn | Value depends on grounding configuration | GEN_GROUNDING_REACTANCE | grounding_configuration = REACTANCE

## 2-Winding Transformer
2-WINDING TRANSFORMER
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_apparent_power | Rated Apparent Power (kVA) | NUMBER | kVA | Yes | Yes
fan_cooled_apparent_power | Fan-Cooled Apparent Power (kVA) | NUMBER | kVA | No | No
primary_voltage | Primary Voltage (kV) | NUMBER | kV | Yes | Yes
secondary_voltage | Secondary Voltage (kV) | NUMBER | kV | Yes | Yes
positive_sequence_impedance | Positive Sequence Impedance (%) | NUMBER | % | Yes | Yes |  | Normal 2-winding impedance
zero_sequence_impedance | Zero Sequence Impedance (%) | NUMBER | % | No | Yes
positive_sequence_x_r | Positive Sequence X/R Ratio | NUMBER |  | Yes | Yes
zero_sequence_x_r | Zero Sequence X/R Ratio | NUMBER |  | No | Yes
primary_connection | Primary Connection | ENUM |  | Yes | Yes | DELTA; WYE; ZIGZAG;
secondary_connection | Secondary Connection | ENUM |  | Yes | Yes | DELTA; WYE; ZIGZAG;
vector_group | Vector Group | TEXT |  | No | No |  | e.g. Dyn11
cooling_class | Cooling Class | TEXT |  | No | No |  | e.g. ONAN, ONAF, AA, FA
temperature_rise | Temperature Rise C | NUMBER | °C | No | No
inrush_current_multiplier | Inrush Current Multiplier | NUMBER |  | No | No |  | Single point; Fallback if inrush curve doesn't exist |  | XFMR_INRUSH_POINT | A single-point inrush representation is supplied.
inrush_current_duration | Inrush Current Duration (s) | NUMBER | s | No | No |  | Single point; Fallback if inrush curve doesn't exist |  | XFMR_INRUSH_POINT | A single-point inrush representation is supplied.
primary_grounding_configuration | Primary Grounding Configuration | ENUM |  | No | Yes | SOLID; RESISTANCE; REACTANCE; UNGROUNDED; UNKNOWN
primary_grounding_resistance | Primary Grounding Resistance (Ω) | NUMBER | Ω | No | Yes |  |  |  | XFMR_PRIMARY_GROUND_R | primary_grounding_configuration = RESISTANCE
primary_grounding_reactance | Primary Grounding Reactance (Ω) | NUMBER | Ω | No | Yes |  |  |  | XFMR_PRIMARY_GROUND_X | primary_grounding_configuration = REACTANCE
secondary_grounding_configuration | Secondary Grounding Configuration | ENUM |  | No | Yes | SOLID; RESISTANCE; REACTANCE; UNGROUNDED; UNKNOWN
secondary_grounding_resistance | Secondary Grounding Resistance (Ω) | NUMBER | Ω | No | Yes |  |  |  | XFMR_SECONDARY_GROUND_R | secondary_grounding_configuration = RESISTANCE
secondary_grounding_reactance | Secondary Grounding Reactance (Ω) | NUMBER | Ω | No | Yes |  |  |  | XFMR_SECONDARY_GROUND_X | secondary_grounding_configuration = REACTANCE

## Bus
BUS
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
bus_type | Bus Type | ENUM |  | Yes | Yes | SWITCHGEAR; SWITCHBOARD; PANELBOARD; MCC; JUNCTION_BOX; OTHER;
nominal_voltage | Nominal Voltage (kV) | NUMBER | kV | Yes | Yes
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | No | No
phase_count | Phase Count | INTEGER |  | No | Yes
short_circuit_current_rating | Short-Circuit Current Rating (kA) | NUMBER | kA | Yes | Yes |  | Typically RMS symmetrical current
short_time_withstand_current | Short-Time Withstand Current (kA) | NUMBER | kA | No | No |  | Typically RMS symmetrical |  | BUS_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-Time Withstand Duration (s) | NUMBER | s | No | No |  |  |  | BUS_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
peak_withstand_current | Peak Withstand Current (kA) | NUMBER | kA | No | No |  | Peak current, not RMS
series_rating_applicable | Series Rating Applicable | BOOLEAN |  | No | Yes
main_protective_device_isolated | Main Protective Device Isolated | BOOLEAN |  | No | Yes |  |  |  | BUS_SERIES_RATING_ISOLATION | series_rating_applicable = TRUE
electrode_configuration | Electrode Configuration | ENUM |  | No | Yes | VCB; VCBB; HCB; VOA; HOA;
electrode_gap | Electrode Gap (mm) | NUMBER | mm | No | No |  | IEEE 1584 electrode gap
enclosure_type | Enclosure Type | TEXT |  | No | No
enclosure_height | Enclosure Height (mm) | NUMBER | mm | No | No
enclosure_width | Enclosure Width (mm) | NUMBER | mm | No | No
enclosure_depth | Enclosure Depth (mm) | NUMBER | mm | No | No
bus_material | Bus Material | ENUM |  | No | No | COPPER; ALUMINUM; OTHER
working_distance | Working Distance (mm) | NUMBER | mm | No | No |  | If bus_type is given, working_distance is usually inferred.

## LV Breaker
LV BREAKER
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
standard | Standard (ANSI/IEC) | ENUM |  | No | No | ANSI; IEC;
manufacturer | Manufacturer | TEXT |  | Yes | Yes |  | Required to determine trip curve.
model | Model | TEXT |  | Yes | Yes |  | Required to determine trip curve.
catalog_number | Catalog Number | TEXT |  | No | Yes
breaker_type | Breaker Type | ENUM |  | No | No | MCB; MCCB; ICCB; ACB; LVPCB; OTHER;
pole_count | Pole Count | INTEGER |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
frame_rating | Frame Rating (A) | NUMBER | A | Yes | Yes |  | Ampere rating of the breaker frame; Deduced if catalog_number is provided.
sensor_rating | Sensor Rating (A) | NUMBER | A | No | Yes |  | Ampere rating of the trip unit sensor; Required for electronic trip breakers. |  | LV_BREAKER_ELECTRONIC_TRIP | trip_unit_type = ELECTRONIC
rating_plug | Rating Plug (A) | NUMBER | A | No | Yes |  | Size of the trip unit plug
trip_rating | Trip Rating (A) | NUMBER | A | No | Yes |  | Trip amps / long-time pickup for thermal magnetic breakers; Required for thermal magnetic breakers. |  | LV_BREAKER_THERMAL_TRIP | trip_unit_type = THERMAL_MAGNETIC
long_time_pickup | Long-Time Pickup (A) | NUMBER | A | No | Yes |  | Long-time pickup for electronic trip breakers; Required for electronic trip breakers. |  | LV_BREAKER_ELECTRONIC_TRIP | trip_unit_type = ELECTRONIC
interrupting_rating | Interrupting Rating (kA) | NUMBER | kA | Yes | Yes |  | Interrupting rating is usually deduced from the breaker model + rated voltage.
trip_unit_type | Trip Unit Type | ENUM |  | Yes | Yes | THERMAL_MAGNETIC; ELECTRONIC; NONE;
trip_unit_model | Trip Unit Model | TEXT |  | No | Yes |  | Required for electronic trip breakers; Required to determine trip curve. |  | LV_BREAKER_ELECTRONIC_TRIP | trip_unit_type = ELECTRONIC
normally_closed | Normally Closed | BOOLEAN |  | No | No

## HV Breaker
HV BREAKER
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
standard | Standard (ANSI/IEC) | ENUM |  | No | No | ANSI; IEC;
manufacturer | Manufacturer | TEXT |  | No | Yes
model | Model | TEXT |  | No | Yes
catalog_number | Catalog Number | TEXT |  | No | No
breaker_type | Breaker Type | ENUM |  | No | No | VCB; SF6; ACB; BOCB; MOCB; OTHER
pole_count | Pole Count | INTEGER |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | Yes | Yes
short_circuit_breaking_current | Short-Circuit Breaking Current (kA) | NUMBER | kA | No | Yes |  | Rated short-circuit interrupting rating - ANSI Rated short-circuit breaking current - IEC | Can be deduced from manufacturer + model.
short_circuit_making_current | Short-Circuit Making Current (kA) | NUMBER | kA | No | Yes |  | Rated closing-and-latching current - ANSI Rated short-circuit making current - IEC | Can be deduced from manufacturer + model.
short_time_withstand_current | Short-time Withstand Current (kA) | NUMBER | kA | No | Yes |  | Short-time current-carrying capability - ANSI Rated short-time withstand current - IEC | Can be deduced from manufacturer + model. | HV_BREAKER_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-time Withstand Duration (s) | NUMBER | s | No | Yes |  | Permissible tripping delay / short-time duration - ANSI Rated short-circuit duration - IEC | Can be deduced from manufacturer + model. | HV_BREAKER_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
rated_interrupting_time | Rated Interrupting Time (s) | NUMBER | s | No | Yes |  | Rated interrupting time - ANSI Rated Break time - IEC | Can be deduced from manufacturer + model.
opening_time | Opening Time (s) | NUMBER | s | No | No |  | Contact-parting time - ANSI Rated opening time - IEC | Can be deduced from manufacturer + model.
closing_time | Closing Time (s) | NUMBER | s | No | No
normally_closed | Normally Closed | BOOLEAN |  | No | No

## Recloser
RECLOSER
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | Yes | Yes
model | Model | TEXT |  | Yes | Yes
controller | Controller | TEXT |  | Yes | Yes
pole_count | Pole Count | INTEGER |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | Yes | Yes
short_circuit_breaking_current | Short-Circuit Breaking Current (kA) | NUMBER | kA | No | Yes
short_circuit_making_current | Short-Circuit Making Current (kA) | NUMBER | kA | No | Yes
short_time_withstand_current | Short-time Withstand Current (kA) | NUMBER | kA | No | Yes |  |  |  | RECLOSER_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-time Withstand Duration (s) | NUMBER | s | No | Yes |  |  |  | RECLOSER_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
rated_interrupting_time | Rated Interrupting Time (s) | NUMBER | s | No | Yes
opening_time | Opening Time (s) | NUMBER | s | No | No
closing_time | Closing Time (s) | NUMBER | s | No | No
normally_closed | Normally Closed | BOOLEAN |  | No | No

## Overcurrent Relay (OCR)
OVERCURRENT RELAY
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | Yes | Yes
model | Model | TEXT |  | Yes | Yes
firmware_version | Firmware Version | TEXT |  | No | Yes
nominal_current_input | Nominal Current Input (A) | NUMBER | A | No | Yes |  | Usually 1 A or 5 A CT input
current_input_burden | Current Input Burden (VA) | NUMBER | VA | No | No
minimum_relay_operating_time | Minimum Relay Operating Time (s) | NUMBER | s | No | No |  | If explicitly published/relevant
trip_output_operating_time | Trip Output Operating Time (s) | NUMBER | s | No | No |  | If separately published

## Fuse
FUSE
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | Yes | Yes |  | Required to determine trip curve.
model | Model | TEXT |  | Yes | Yes |  | Required to determine trip curve.
catalog_number | Catalog Number | TEXT |  | No | No
rated_voltage | Rated Voltage | NUMBER | kV | No | No
current_rating | Current Rating A | NUMBER | A | Yes | Yes |  | Can be deduced from catalog number.
interrupting_rating | Interrupting Rating kA | NUMBER | kA | No | Yes |  | Can be deduced from manufacturer + model.
fuse_class | Fuse Class | TEXT |  | No | Yes |  | Can be deduced from manufacturer + model.
fuse_speed | Fuse Speed | ENUM |  | No | Yes | VERY_FAST; FAST; QUICK; STANDARD; TIME_DELAY; LONG_TIME_DELAY; OTHER; | Can be deduced from manufacturer + model.
current_limiting | Current Limiting | BOOLEAN |  | No | Yes

## Single-Throw Switch
SINGLE-THROW SWITCH
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions. Canonical type name/meaning is provisional.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
rated_voltage | Rated Voltage (kV) | NUMBER | kV | No | No
continuous_current_rating | Continuous Current (A) | NUMBER | A | No | No
short_time_withstand_current | Short-time Withstand Current (kA) | NUMBER | kA | No | No |  |  |  | SWITCH_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-time Withstand Duration (s) | NUMBER | s | No | No |  |  |  | SWITCH_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
peak_withstand_current | Peak Withstand Current (kA) | NUMBER | kA | No | Yes |  | Peak instantaneous current withstand capability, including DC offset effects; do not interpret as RMS symmetrical current.
short_circuit_current_rating | Short-Circuit Current Rating (kA) | NUMBER | kA | Yes | Yes
load_break_capable | Load Break Capable | BOOLEAN |  | No | No
normally_closed | Normally Closed | BOOLEAN |  | No | No

## Double-Throw Switch
DOUBLE-THROW SWITCH (ATS or MTS)
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions. Assumed to mean double-throw / transfer switch; please confirm.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | No | No
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | No | No
pole_count | Pole Count | INTEGER |  | No | No
neutral_pole_type | Neutral Pole Type | ENUM |  | No | No | SOLID; SWITCHED; OVERLAPPING; NONE;
operation_type | Operation Type | ENUM |  | No | No | MANUAL; AUTOMATIC;
transition_type | Transition Type | ENUM |  | No | No | OPEN_TRANSITION; CLOSED_TRANSITION; DELAYED_TRANSITION; SOFT_LOAD_TRANSITION;
short_time_withstand_current | Short-time Withstand Current (kA) | NUMBER | kA | No | No |  |  |  | DTS_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-time Withstand Duration (s) | NUMBER | s | No | No |  |  |  | DTS_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
peak_withstand_current | Peak Withstand Current (kA) | NUMBER | kA | No | Yes |  | Peak instantaneous current withstand capability, including DC offset effects; do not interpret as RMS symmetrical current.
short_circuit_current_rating | Short-Circuit Current Rating (kA) | NUMBER | kA | Yes | Yes
withstand_closing_current_rating | Withstand Closing Current Rating (kA) | NUMBER | kA | No | Yes |  |  |  | DTS_WITHSTAND_CLOSING_PAIR | Either withstand-closing field is supplied.
withstand_closing_duration | Withstand Closing Duration (s) | NUMBER | s | No | Yes |  |  |  | DTS_WITHSTAND_CLOSING_PAIR | Either withstand-closing field is supplied.
rated_transfer_time | Transfer Time (s) | NUMBER | s | No | No
load_break_capable | Load Break Capable | BOOLEAN |  | No | No

## Cable
CABLE
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_voltage | Voltage Rating (kV) | NUMBER | kV | No | No
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | No | No
length | Length (m) | NUMBER | m | Yes | Yes
conductor_material | Conductor Material (Al or Cu) | ENUM |  | No | Yes | COPPER; ALUMINUM; |  |  | CABLE_ELECTRICAL_DEFINITION:A | Always for a study-ready cable model, in addition to length.
conductor_size | Conductor Size | TEXT |  | No | Yes |  | e.g. 4/0 AWG, 500 kcmil, 240 mm² |  | CABLE_ELECTRICAL_DEFINITION:A | Always for a study-ready cable model, in addition to length.
core_count_per_cable | Core Count Per Cable | INTEGER |  | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:A | Always for a study-ready cable model, in addition to length.
parallel_run_count | Parallel Run Count | INTEGER |  | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:A | Always for a study-ready cable model, in addition to length.
insulation_material | Insulation Material | TEXT |  | No | Yes |  | e.g. XLPE
positive_sequence_resistance | Positive Sequence Resistance (Ω/km) | NUMBER | Ω/km | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:B | Always for a study-ready cable model, in addition to length.
positive_sequence_reactance | Positive Sequence Reactance (Ω/km) | NUMBER | Ω/km | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:B | Always for a study-ready cable model, in addition to length.
zero_sequence_resistance | Zero Sequence Resistance (Ω/km) | NUMBER | Ω/km | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:B | Always for a study-ready cable model, in addition to length.
zero_sequence_reactance | Zero Sequence Reactance (Ω/km) | NUMBER | Ω/km | No | Yes |  |  |  | CABLE_ELECTRICAL_DEFINITION:B | Always for a study-ready cable model, in addition to length.

## CT
CT
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
primary_current | Primary Current (A) | NUMBER | A | Yes | Yes
secondary_current | Secondary Current (A) | NUMBER | A | Yes | Yes
accuracy_class | Accuracy Class | TEXT |  | No | No
rated_burden | Rated Burden (VA) | NUMBER | VA | No | No

## Induction Motor
INDUCTION MOTOR
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_active_power | Rated Active Power (kW) | NUMBER | kW | Yes | Yes
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
full_load_current | Full Load Current (A) | NUMBER | A | No | Yes |  |  |  | MOTOR_APPARENT_POWER_BASIS:A | Apparent-power base is needed and is not otherwise imported/derived.
rated_speed | Rated Speed (rpm) | NUMBER | rpm | No | No
rated_slip | Slip (%) | NUMBER | % | No | No
phase_count | Phase Count | INTEGER |  | No | Yes
pole_count | Pole Count | INTEGER |  | No | No
efficiency | Efficiency (%) | NUMBER | % | No | Yes |  |  |  | MOTOR_APPARENT_POWER_BASIS:B | Apparent-power base is needed and is not otherwise imported/derived.
power_factor | Power Factor | NUMBER |  | No | Yes |  |  |  | MOTOR_APPARENT_POWER_BASIS:B | Apparent-power base is needed and is not otherwise imported/derived.
service_factor | Service Factor | NUMBER |  | No | No
starting_time | Starting Time (s) | NUMBER | s | No | Yes
locked_rotor_current | Locked Rotor Current (A) | NUMBER | A | No | Yes
locked_rotor_power_factor | Locked Rotor Power Factor | NUMBER |  | No | No
subtransient_reactance | Subtransient Reactance (p.u.) | NUMBER | p.u. | No | Yes |  | X''
subtransient_x_r | Subtransient X/R Ratio | NUMBER |  | No | Yes |  | X''/R
subtransient_time_constant | Subtransient Time Constant (s) | NUMBER | s | No | Yes |  | T''; Needed if time decay of motor fault contribution is modeled
negative_sequence_reactance | Negative Sequence Reactance (p.u.) | NUMBER | p.u. | No | Yes |  | X2; Needed for applicable unbalanced-fault calculations
zero_sequence_reactance | Zero Sequence Reactance (p.u.) | NUMBER | p.u. | No | Yes |  | X0; Needed only when a zero-sequence path exists and ground faults are modeled

## Static Load
STATIC LOAD
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
rated_active_power | Rated Active Power (kW) | NUMBER | kW | No | Yes |  | Alternative load-power representation; see Requirement Rules. |  | STATIC_LOAD_POWER_DEFINITION:B | Always for a study-ready static load.
rated_reactive_power | Rated Reactive Power (kvar) | NUMBER | kvar | No | Yes |  | Alternative load-power representation; see Requirement Rules. |  | STATIC_LOAD_POWER_DEFINITION:B | Always for a study-ready static load.
rated_apparent_power | Rated Apparent Power (kVA) | NUMBER | kVA | No | Yes |  | Alternative load-power representation; see Requirement Rules. |  | STATIC_LOAD_POWER_DEFINITION:A | Always for a study-ready static load.
rated_current | Rated Current (A) | NUMBER | A | No | Yes
power_factor | Power Factor | NUMBER |  | No | Yes |  | Required with rated_apparent_power when using the kVA + PF representation. |  | STATIC_LOAD_POWER_DEFINITION:A | Always for a study-ready static load.
phase_count | Phase Count | INTEGER |  | No | Yes

## Lumped Load
LUMPED_LOAD
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
rated_current | Rated Current (A) | NUMBER | A | No | No
rated_active_power | Rated Active Power (kW) | NUMBER | kW | Yes | Yes
rated_apparent_power | Rated Apparent Power (kVA) | NUMBER | kVA | No | Yes |  |  |  | LUMPED_LOAD_POWER_DEFINITION:A | Always, in addition to the required rated_active_power.
power_factor | Power Factor | NUMBER |  | No | Yes |  |  |  | LUMPED_LOAD_POWER_DEFINITION:B | Always, in addition to the required rated_active_power.
phase_count | Phase Count | INTEGER |  | No | No
motor_load_percent | Motor Load Percent (%) | NUMBER | % | No | Yes

## Capacitor
CAPACITOR
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
bank_count | Bank Count | INTEGER |  | No | No
capacitors_per_bank | Capacitors Per Bank | INTEGER |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
rated_reactive_power | Rated Reactive Power (kvar) | NUMBER | kvar | Yes | Yes
rated_current | Rated Current (A) | NUMBER | A | No | No
rated_capacitance | Rated Capacitance (µF) | NUMBER | µF | No | No
phase_count | Phase Count | INTEGER |  | No | No
connection_type | Connection Type | ENUM |  | No | Yes | DELTA; WYE;
neutral_grounding_type | Neutral Grounding Type | ENUM |  | No | Yes | SOLID; UNGROUNDED; NONE; |  |  | CAPACITOR_WYE_GROUNDING | connection_type = WYE
discharge_resistance | Discharge Resistance (Ω) | NUMBER | Ω | No | No
short_circuit_current_rating | Short-Circuit Current Rating (kA) | NUMBER | kA | No | No

## Reactor
REACTOR
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
reactor_type | Reactor Type | ENUM |  | Yes | Yes | SERIES; SHUNT; CURRENT_LIMITING; NEUTRAL_GROUNDING; FILTER; OTHER;
phase_count | Phase Count | INTEGER |  | No | No
rated_voltage | Rated Voltage (kV) | NUMBER | kV | Yes | Yes
continuous_current_rating | Continuous Current Rating (A) | NUMBER | A | No | No
rated_reactive_power | Rated Reactive Power (kvar) | NUMBER | kvar | No | Yes |  |  |  | REACTOR_SHUNT_RATING | reactor_type = SHUNT
positive_sequence_impedance | Positive Sequence Impedance (Ω) | NUMBER | Ω | No | Yes |  |  |  | REACTOR_SERIES_IMPEDANCE:A | reactor_type IN {SERIES, CURRENT_LIMITING, FILTER}
zero_sequence_impedance | Zero Sequence Impedance (Ω) | NUMBER | Ω | No | Yes
neutral_grounding_impedance | Neutral Grounding Impedance (Ω) | NUMBER | Ω | No | Yes |  |  |  | REACTOR_NEUTRAL_GROUNDING | reactor_type = NEUTRAL_GROUNDING
positive_sequence_x_r | Positive Sequence X/R Ratio | NUMBER |  | No | Yes
zero_sequence_x_r | Zero Sequence X/R Ratio | NUMBER |  | No | Yes
neutral_grounding_x_r | Neutral Grounding X/R Ratio | NUMBER |  | No | No
impedance_tolerance | Impedance Tolerance (%) | NUMBER | % | No | Yes
rated_inductance | Rated Inductance (mH) | NUMBER | mH | No | Yes |  |  |  | REACTOR_SERIES_IMPEDANCE:B | reactor_type IN {SERIES, CURRENT_LIMITING, FILTER}
short_time_withstand_current | Short-time Withstand Current (kA) | NUMBER | kA | No | No |  |  |  | REACTOR_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
short_time_withstand_duration | Short-time Withstand Duration (s) | NUMBER | s | No | No |  |  |  | REACTOR_SHORT_TIME_PAIR | Either short-time withstand field is supplied.
peak_withstand_current | Peak Withstand Current (kA) | NUMBER | kA | No | No
connection_type | Connection Type | ENUM |  | No | Yes | DELTA; WYE; |  |  | REACTOR_CONNECTION | reactor_type IN {SHUNT, FILTER}

## VFD
VFD
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
rated_active_power | Rated Active Power (kW) | NUMBER | kW | No | No
rated_input_voltage | Rated Input Voltage (kV) | NUMBER | kV | Yes | Yes
rated_output_voltage | Rated Output Voltage (kV) | NUMBER | kV | Yes | Yes
rated_input_current | Rated Input Current (A) | NUMBER | A | No | No
rated_output_current | Rated Output Current (A) | NUMBER | A | No | No
short_circuit_current_rating | Short-Circuit Current Rating (kA) | NUMBER | kA | Yes | Yes
bypass_available | Bypass Available | BOOLEAN |  | No | Yes
front_end_type | Front-End Type | ENUM |  | Yes | Yes | DIODE_RECTIFIER; THYRISTOR_RECTIFIER; ACTIVE_FRONT_END; OTHER;
regenerative_capable | Regenerative Capable | BOOLEAN |  | No | No
output_short_circuit_current | Output Short-Circuit Current (A) | NUMBER | A | No | Yes |  |  |  | VFD_OUTPUT_FAULT_DEFINITION:A | Output-side VFD short-circuit contribution is explicitly modeled.
output_short_circuit_current_multiplier | Output Short-Circuit Current Multiplier | NUMBER |  | No | No |  |  |  | VFD_OUTPUT_FAULT_DEFINITION:B | Output-side VFD short-circuit contribution is explicitly modeled.
output_short_circuit_duration | Output Short-Circuit Duration (s) | NUMBER | s | No | No
output_short_circuit_trip_time | Output Short-Circuit Trip Time (ms) | NUMBER | ms | No | No
upstream_short_circuit_contribution | Upstream Short-Circuit Contribution (A) | NUMBER | A | No | Yes

## UPS
UPS
Edit any proposed registry field directly. Use Reviewer Notes to record your decisions.
Key | Display Name | Value Type | Canonical Unit | Required? | Critical? | Allowed / Enum Values | Notes | Reviewer Notes | Requirement Group | Requirement Condition
manufacturer | Manufacturer | TEXT |  | No | No
model | Model | TEXT |  | No | No
ups_topology | UPS Topology | ENUM |  | Yes | No | ONLINE_DOUBLE_CONVERSION; LINE_INTERACTIVE; OFFLINE_STANDBY; OTHER;
rated_input_voltage | Rated Input Voltage (kV) | NUMBER | kV | Yes | Yes
rated_output_voltage | Rated Output Voltage (kV) | NUMBER | kV | Yes | Yes
input_phase_count | Input Phase Count | INTEGER |  | No | Yes
output_phase_count | Output Phase Count | INTEGER |  | No | Yes
rated_output_apparent_power | Rated Output Apparent Power | NUMBER | kVA | Yes | Yes
rated_input_current | Rated Input Current | NUMBER | A | No | No
maximum_input_current | Maximum Input Current | NUMBER | A | No | No
rated_output_current | Rated Output Current | NUMBER | A | No | No
input_short_circuit_current_rating | Input Short-Circuit Current Rating (kA) | NUMBER | kA | No | Yes
output_short_circuit_current | Output Short-Circuit Current (A) | NUMBER | A | No | Yes |  |  |  | UPS_INVERTER_FAULT_CURRENT | UPS inverter-mode short-circuit contribution is explicitly modeled and cannot be inferred from manufacturer/model data.
output_short_circuit_duration | Output Short-Circuit Duration (s) | NUMBER | s | No | No
output_short_circuit_trip_time | Output Short-Circuit Trip Time (ms) | NUMBER | ms | No | No
upstream_short_circuit_contribution | Upstream Short-Circuit Contribution (A) | NUMBER | A | No | Yes
static_bypass_available | Static Bypass Available | BOOLEAN |  | Yes | Yes
separate_bypass_input | Separate Bypass Input | BOOLEAN |  | No | Yes |  |  |  | UPS_STATIC_BYPASS_INPUT | static_bypass_available = TRUE
rated_bypass_current | Rated Bypass Current | NUMBER | A | No | Yes |  |  |  | UPS_STATIC_BYPASS_RATING | static_bypass_available = TRUE
bypass_short_circuit_current_rating | Bypass Short-Circuit Current Rating (kA) | NUMBER | kA | No | Yes |  |  |  | UPS_STATIC_BYPASS_RATING | static_bypass_available = TRUE
bypass_short_time_withstand_current | Bypass Short-time Withstand Current (kA) | NUMBER | kA | No | No |  |  |  | UPS_BYPASS_SHORT_TIME_PAIR | Either bypass short-time withstand field is supplied.
bypass_short_time_withstand_duration | Bypass Short-time Withstand Duration (s) | NUMBER | s | No | No |  |  |  | UPS_BYPASS_SHORT_TIME_PAIR | Either bypass short-time withstand field is supplied.
fault_transfer_to_bypass_time | Fault Transfer To Bypass Time (ms) | NUMBER | ms | No | No

## Requirement Rules
Equipment Type | Rule ID | Rule Type | Condition | Alternative | Attributes | Engineering Rationale | Implementation Note
Utility Source | UTILITY_FAULT_DATA | ANY_OF | Always for a study-ready utility short-circuit source. | A | three_phase_fault_current; slg_fault_current; three_phase_x_r; slg_x_r | Direct fault-current + X/R representation. | For ANY_OF: one complete alternative must be satisfied.
Utility Source | UTILITY_FAULT_DATA | ANY_OF | Always for a study-ready utility short-circuit source. | B | positive_sequence_resistance; positive_sequence_reactance; zero_sequence_resistance; zero_sequence_reactance | Sequence-impedance representation. | For ANY_OF: one complete alternative must be satisfied.
Synchronous Generator | GEN_REACTANCE_BASE_POWER | REQUIRED_IF | Per-unit reactances are stated on a base power different from rated_apparent_power. |  | reactance_base_power | Needed to convert per-unit reactances to the canonical machine base. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Synchronous Generator | GEN_REACTANCE_BASE_VOLTAGE | REQUIRED_IF | Per-unit reactances are stated on a base voltage different from rated_voltage. |  | reactance_base_voltage | Needed to convert per-unit reactances to the canonical machine base. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Synchronous Generator | GEN_GROUNDING_RESISTANCE | REQUIRED_IF | grounding_configuration = RESISTANCE |  | grounding_resistance | Resistance-grounded neutral requires the grounding resistance. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Synchronous Generator | GEN_GROUNDING_REACTANCE | REQUIRED_IF | grounding_configuration = REACTANCE |  | grounding_reactance | Reactance-grounded neutral requires the grounding reactance. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
2-Winding Transformer | XFMR_PRIMARY_GROUND_R | REQUIRED_IF | primary_grounding_configuration = RESISTANCE |  | primary_grounding_resistance | Primary neutral resistance is required when resistance grounded. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
2-Winding Transformer | XFMR_PRIMARY_GROUND_X | REQUIRED_IF | primary_grounding_configuration = REACTANCE |  | primary_grounding_reactance | Primary neutral reactance is required when reactance grounded. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
2-Winding Transformer | XFMR_SECONDARY_GROUND_R | REQUIRED_IF | secondary_grounding_configuration = RESISTANCE |  | secondary_grounding_resistance | Secondary neutral resistance is required when resistance grounded. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
2-Winding Transformer | XFMR_SECONDARY_GROUND_X | REQUIRED_IF | secondary_grounding_configuration = REACTANCE |  | secondary_grounding_reactance | Secondary neutral reactance is required when reactance grounded. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
2-Winding Transformer | XFMR_INRUSH_POINT | ALL_OR_NONE | A single-point inrush representation is supplied. |  | inrush_current_multiplier; inrush_current_duration | The multiplier and its duration describe one inrush point and should be supplied together. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Bus | BUS_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Bus | BUS_SERIES_RATING_ISOLATION | REQUIRED_IF | series_rating_applicable = TRUE |  | main_protective_device_isolated | Series-rated equipment evaluation needs the upstream/main protective-device relationship. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
LV Breaker | LV_BREAKER_THERMAL_TRIP | REQUIRED_IF | trip_unit_type = THERMAL_MAGNETIC |  | trip_rating | Thermal-magnetic breakers use the fixed trip rating as the long-time current basis. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
LV Breaker | LV_BREAKER_ELECTRONIC_TRIP | ALL_OF | trip_unit_type = ELECTRONIC |  | sensor_rating; long_time_pickup; trip_unit_model | Electronic-trip modeling needs the sensor basis, long-time pickup, and trip-unit model. rating_plug remains conditional on designs that use one. | For ALL_OF: every listed attribute is required when the condition is true.
HV Breaker | HV_BREAKER_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Recloser | RECLOSER_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Single-Throw Switch | SWITCH_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Double-Throw Switch | DTS_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Double-Throw Switch | DTS_WITHSTAND_CLOSING_PAIR | ALL_OR_NONE | Either withstand-closing field is supplied. |  | withstand_closing_current_rating; withstand_closing_duration | Withstand/closing current must be associated with its applicable duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
Cable | CABLE_ELECTRICAL_DEFINITION | ANY_OF | Always for a study-ready cable model, in addition to length. | A | conductor_material; conductor_size; core_count_per_cable; parallel_run_count | Physical-construction representation from which impedance can be calculated/selected. | For ANY_OF: one complete alternative must be satisfied.
Cable | CABLE_ELECTRICAL_DEFINITION | ANY_OF | Always for a study-ready cable model, in addition to length. | B | positive_sequence_resistance; positive_sequence_reactance; zero_sequence_resistance; zero_sequence_reactance | Direct sequence-impedance representation. | For ANY_OF: one complete alternative must be satisfied.
Induction Motor | MOTOR_APPARENT_POWER_BASIS | ANY_OF | Apparent-power base is needed and is not otherwise imported/derived. | A | full_load_current | Voltage + full-load current can establish the apparent-power base. | For ANY_OF: one complete alternative must be satisfied.
Induction Motor | MOTOR_APPARENT_POWER_BASIS | ANY_OF | Apparent-power base is needed and is not otherwise imported/derived. | B | efficiency; power_factor | Rated active power + efficiency + power factor can establish the apparent-power base. | For ANY_OF: one complete alternative must be satisfied.
Static Load | STATIC_LOAD_POWER_DEFINITION | ANY_OF | Always for a study-ready static load. | A | rated_apparent_power; power_factor | Apparent-power + PF representation. | For ANY_OF: one complete alternative must be satisfied.
Static Load | STATIC_LOAD_POWER_DEFINITION | ANY_OF | Always for a study-ready static load. | B | rated_active_power; rated_reactive_power | Active/reactive-power representation. | For ANY_OF: one complete alternative must be satisfied.
Lumped Load | LUMPED_LOAD_POWER_DEFINITION | ANY_OF | Always, in addition to the required rated_active_power. | A | rated_apparent_power | Rated active + apparent power determines PF/reactive power. | For ANY_OF: one complete alternative must be satisfied.
Lumped Load | LUMPED_LOAD_POWER_DEFINITION | ANY_OF | Always, in addition to the required rated_active_power. | B | power_factor | Rated active power + PF determines apparent/reactive power. | For ANY_OF: one complete alternative must be satisfied.
Capacitor | CAPACITOR_WYE_GROUNDING | REQUIRED_IF | connection_type = WYE |  | neutral_grounding_type | A wye-connected bank must identify whether the neutral is solidly grounded, ungrounded, or otherwise not grounded. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Reactor | REACTOR_SHUNT_RATING | REQUIRED_IF | reactor_type = SHUNT |  | rated_reactive_power | Shunt reactors are conventionally specified by reactive-power rating at rated voltage. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Reactor | REACTOR_SERIES_IMPEDANCE | ANY_OF | reactor_type IN {SERIES, CURRENT_LIMITING, FILTER} | A | positive_sequence_impedance | Direct impedance representation. | For ANY_OF: one complete alternative must be satisfied.
Reactor | REACTOR_SERIES_IMPEDANCE | ANY_OF | reactor_type IN {SERIES, CURRENT_LIMITING, FILTER} | B | rated_inductance | Inductance representation; impedance is frequency-dependent and can be derived when frequency is known. | For ANY_OF: one complete alternative must be satisfied.
Reactor | REACTOR_NEUTRAL_GROUNDING | REQUIRED_IF | reactor_type = NEUTRAL_GROUNDING |  | neutral_grounding_impedance | Neutral-grounding reactors are defined by the grounding impedance. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Reactor | REACTOR_CONNECTION | REQUIRED_IF | reactor_type IN {SHUNT, FILTER} |  | connection_type | Connection affects network and zero-sequence behavior. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Reactor | REACTOR_SHORT_TIME_PAIR | ALL_OR_NONE | Either short-time withstand field is supplied. |  | short_time_withstand_current; short_time_withstand_duration | A short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
VFD | VFD_OUTPUT_FAULT_DEFINITION | ANY_OF | Output-side VFD short-circuit contribution is explicitly modeled. | A | output_short_circuit_current | Direct output fault-current representation. | For ANY_OF: one complete alternative must be satisfied.
VFD | VFD_OUTPUT_FAULT_DEFINITION | ANY_OF | Output-side VFD short-circuit contribution is explicitly modeled. | B | output_short_circuit_current_multiplier | Multiplier representation when vendor data is expressed relative to rated output current. | For ANY_OF: one complete alternative must be satisfied.
UPS | UPS_STATIC_BYPASS_INPUT | REQUIRED_IF | static_bypass_available = TRUE |  | separate_bypass_input | Defines whether the bypass shares the rectifier input or has a separate source. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
UPS | UPS_STATIC_BYPASS_RATING | ALL_OF | static_bypass_available = TRUE |  | rated_bypass_current; bypass_short_circuit_current_rating | Bypass-mode load capacity and short-circuit withstand/rating are needed when the bypass path exists. | For ALL_OF: every listed attribute is required when the condition is true.
UPS | UPS_BYPASS_SHORT_TIME_PAIR | ALL_OR_NONE | Either bypass short-time withstand field is supplied. |  | bypass_short_time_withstand_current; bypass_short_time_withstand_duration | A bypass short-time current rating is meaningful only with its duration. | For ALL_OR_NONE: if any listed attribute is supplied, all listed attributes must be supplied.
UPS | UPS_INVERTER_FAULT_CURRENT | REQUIRED_IF | UPS inverter-mode short-circuit contribution is explicitly modeled and cannot be inferred from manufacturer/model data. |  | output_short_circuit_current | Needed to represent current-limited inverter contribution. | For REQUIRED_IF: the listed attribute(s) become required when the condition is true.
Overcurrent Relay (OCR) | NONE | NONE | No equipment-configuration conditional requirements identified in registry-v1. |  |  | Individual Required? flags apply directly.
Fuse | NONE | NONE | No equipment-configuration conditional requirements identified in registry-v1. |  |  | Individual Required? flags apply directly.
CT | NONE | NONE | No equipment-configuration conditional requirements identified in registry-v1. |  |  | Individual Required? flags apply directly.

## Research Sources
Topic | Source | URL | Relevance to Registry
Cable modeling / alternative impedance representation | EasyPower Cable - Specifications 1 | https://help.easypower.com/ezp/26.0/Content/13_Database_Technical_Ref/Cable/Specifications_1_Tab.htm | Supports physical cable construction/parallel-run inputs and direct positive/zero-sequence R/X entry.
Motor apparent-power basis | EasyPower Motor kVA Calculations | https://help.easypower.com/ezp/26.0/Content/13_Database_Technical_Ref/Motor/Motor_kVA_Calculations.htm | Documents FLA-based kVA calculation or kW with efficiency and power factor.
Motor data / starting parameters | ETAP Motor Parameter Estimation | https://etap.com/product/motor-parameter-estimation-software | Supports locked-rotor current/PF, full-load PF/efficiency/slip and other motor characteristics as modeling inputs.
Static/load power representation | EasyPower Load Data | https://help.easypower.com/ezp/10.3/Content/13_Database_Technical_Ref/dtr_Load_Data.htm | Documents load representation in active and reactive power components.
kVA + power factor load representation | EasyPower Revit Load Import | https://help.easypower.com/ezp/26.0/Content/12_Using_EasyPower_w_Other_Programs/Revit/Import_Load.htm | Documents kVA @ PF as an alternate load representation.
Current-limiting reactor representation | EasyPower CL Reactor - Specifications | https://help.easypower.com/ezp/26.0/Content/13_Database_Technical_Ref/CL_Reactor/Specifications_Tab.htm | Documents alternative reactor impedance inputs and use of sequence impedance/X-R data.
Shunt reactor rating | IEEE Technology Navigator - Shunt Reactors | https://technav.ieee.org/topic/shunt-reactors/ | Notes that shunt-reactor rating is expressed as reactive power (Mvar), supporting type-dependent kvar requirement.
UPS short-circuit representation | EasyPower UPS - Specifications | https://help.easypower.com/ezp/10.6/content/13_database_technical_ref/UPS/Specifications_Tab.htm | Documents current-limited UPS output short-circuit contribution and time-dependent contribution values.
Short-circuit model input expectations | ETAP CSI Power System Study Specification | https://etap.com/docs/default-source/power-systems-study-specification/etap-csi-new-specification-template.pdf?sfvrsn=d944567c_8 | Lists source impedance, conductor lengths/counts/impedances, transformer impedance/X-R and motor contributions among short-circuit model inputs.